## Slide 1: SizeCap: Efficiently Handling Power Surges for Fuel Cell Powered Data Centers
Yang Li, Di Wang, Saugata Ghose, Jie Liu,
Sriram Govindan, Sean James, Eric Peterson,
John Siegler, Rachata Ausavarungnirun, Onur Mutlu
Notes: Thank you for the introduction.
Today I will introduce our work, called SizeCap, which looks at how to efficiently deal with power surges in data centers powered by fuel cells.
This is joint work with my collaborators from Carnegie Mellon and Microsoft Research.

## Slide 2: Executive Summary
Fuel cells: efficient power source for data centers
Problem: limited load following capability
  Fuel cells only gradually increase output power when load increases
  Power surges may lead to a power shortfall  server shutdown or damage
Existing Approaches
  Power capping: hurts performance
  Energy storage device (ESD): increases cost
Our Approach: SizeCap
  Our goal: low cost, still guarantee workload performance
  Key Idea 1: Size the ESD to cover only typical-case power surges
  Key Idea 2: Use smart power capping, which is aware of fuel cell and workload behavior, to handle remaining power surges
  SizeCap safely reduces ESD size by 50 – 85%
Notes: Today, data centers consume a large amount of power, which is driving the need to improve their efficiency.
Fuel cells can be used as an efficient power source.
*X* However, they suffer from what is known as limited load following capability.
*X* This means that a fuel cell can only gradually increase its power output when the power demanded from it increases.
*X* In cases where the power demand increases suddenly, which we call a power surge, the fuel cell may not be able to deliver enough power. We call this a power shortfall, and it can force servers to shut down, or worse, can damage them.
*X* While prior work can mitigate power shortfalls for traditional power sources, we find that they do not work well when used with fuel cells.
*X* One approach, power capping, limits the maximum power of each server. This is conservative, and can hurt performance.
*X* Another approach uses an energy storage device to buffer charge, delivering the charge when a shortfall is about to occur. Unfortunately, large ESDs are expensive, and can significantly increase data center costs.
*X* To provide an efficient approach to handling power shortfalls, we propose SizeCap.
*X* Our goal is to do so at low cost, while still guaranteeing workload performance. There are two key ideas behind SizeCap.
*X* First, we use much smaller ESDs, sizing them so that they hold only enough charge to cover typical-case power surges instead of the rare worst-case surges.
*X* Second, to handle worst-case surges, we use smart power capping, which improves performance by incorporating knowledge of the fuel cell and workload behavior.
*X* As we will see, SizeCap can reduce the size of the ESD by 50 to 85%, without violating any service level agreements for performance.

## Slide 3: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: First, let’s look at a brief background.

## Slide 4: Fuel Cell Powered Data Centers
Data center power consumption continues to grow
  In USA alone:
  We need more energy-efficient power sources
Fuel cells
  Convert fuel (e.g., hydrogen, natural gas) into electricity
  Advantages: high energy efficiency, low CO2 emission,
  highly reliable delivery infrastructure
91 billion kWh @2013
 140 billion kWh @2020
Server 1
Fuel
Cell
System
Rack
.
.
.
Server N
Notes: Data center power consumption has been growing over the last several years.
*X* In the USA alone, data centers consumed 91 billion kilowatt hours in 2013.
*X* This is expected to grow to 140 billion kilowatt hours by 2020.
*X* In order to combat this increasing consumption, we want to find more energy-efficient power sources for data centers.
*X* Fuel cells are a viable alternative power source. They use an electrochemical process to convert some type of fuel into electricity.
*X* Fuel cells have several advantages – they have high energy efficiency, they have low carbon dioxide emission, and they have a highly reliable delivery infrastructure.
Thanks to these advantages, mainstream data center owners are investigating how to integrate fuel cells.
*X* In this work, we use an example system with a fuel cell powering a single rack of servers, as has been prototyped by Microsoft.

## Slide 5: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: While fuel cells are promising, they have a fundamental problem,

## Slide 6: Problem: Limited Load Following Capability
Fuel cell power output only gradually increases when power demand increases
Can lead to server damage or shut down
Power Shortfall
How can we efficiently handle power shortfalls?
Power Shortfall
Notes: Which we call limited load following capability. Due to mechanical limitations, fuel cells can only slowly increase their power output when the load, or the power demanded from them, increases.
*X* Let’s look at a few examples of this. In this graph, the x-axis shows time, and the y-axis shows power. We plot an example of the power demanded by the rack. In this case, the power demand ramps up slowly.
*X* The rate is low enough for the fuel cell output to keep up with the ramp rate.
*X* If the power demand increases at a faster rate,
*X* the fuel cell cannot immediately deliver enough power to keep up with the demand.
*X* This leads to a power shortfall.
*X* As the power demand increase becomes even faster,
*X* the size of the shortfall grows.
*X* These power shortfalls can force servers to shut down, or worse, can damage the servers.
*X* As a result, we need to find a way to efficiently handle these shortfalls.

## Slide 7: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: First, let’s look at two prior approaches to mitigating power shortfalls.

## Slide 8: Existing Approaches to Handling Power Shortfalls
Power capping
  Cuts down the power demand
  Performs DVFS or shuts down nodes
  Low cost
  Hurts performance
Energy storage device (ESD)
  Buffers energy
  Supplies extra energy when needed
  High performance
  High cost: ESD is sized to handle worst-case power surges, even though they rarely occur
Our goal: high performance, low cost
Cost
Performance
ESD
Power
Capping
Our
Goal
Notes:   One approach is known as power capping,
  *X* where we cut down the power demand.
  *X* Power capping can be achieved by either performing DVFS in a server, or by shutting down some of the nodes in a rack.
  *X* Let’s see how power capping performs with respect to two key trade-offs:
  *X* performance, which we show on the x-axis,
  *X* and cost, which we show on the y-axis. Note that for cost, lower is better.
  *X* As we see with power capping,
  *X* it has low cost due to its simplicity, but its approaches are very conservative,
  *X* and can significantly hurt performance.
  *X* A second approach is to use an energy storage device, which buffers energy for use in avoiding shortfalls. When a shortfall is imminent, the ESD supplies extra energy to make up the difference.
  *X* As we see in our trade-off space,
  *X* ESDs can keep performance high, but they come at a high cost.
  *X* To ensure that shortfalls never occur, an ESD is sized to handle the worst-case power surge, even though worst-case surges demand much more power than typical power surges. While the worst case rarely occurs, it forces us to keep the ESD capacity large.
  *X* Our goal is to design a solution that avoids these pitfalls,
  *X* maintaining high performance at a low cost.

## Slide 9: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: To this end, we propose SizeCap.

## Slide 10: SizeCap: Key Ideas
Key Idea 1: Size ESD based on typical-case power surges, not worst-case surges
Key Idea 2: Use smart power capping to handle remaining power surges
Notes: SizeCap is based upon two key ideas. First, we size the ESD to cover power shortfalls only for typical-case power surges, as opposed to the rare worst-case surges. This allows us to greatly reduce the size of the ESD. Second, when those rare worst-case surges occur, we use smart power capping to handle them.
*X* Now let’s examine the first key idea in detail.

## Slide 11: Key Idea 1: Size ESD Based on Typical Case
We study production data center traces from Microsoft
Unavailable period: time that underprovisioned ESD cannot handle power surges
Trace 1: reduce ESD size by 85%  only 0.4% unavailable period
Notes: For our work, we collected rack power demand traces from a production data center at Microsoft.
*X* Here, we study two of these traces, which we plot with time on the x-axis and rack power on the y-axis. In Trace 1, we see infrequent but large power surges. Let’s see what happens when we reduce the size of the ESD.
*X* We study the rack’s unavailable period, defined as the time that the underprovisioned ESD is unable to handle power surges.
*X* On the right, we plot the unavailable period on the y-axis, and show the ESD capacity on the x-axis. As we see, an ESD sized to handle the worst-case power surge in Trace 1 is very large.
*X* Since this surge is very infrequent, we can reduce the ESD capacity by as much as 85% to cover only typical-case surges. Even with such a large reduction, we experience unavailability for only 0.4% of the time.

## Slide 12: Key Idea 1: Size ESD Based on Typical Case
We study production data center traces from Microsoft
Trace 2: reduce ESD size by 50%  6.2% unavailable period
Sizing ESD based on typical-case power surges
does not hurt performance significantly
Notes: Let’s look at another trace. Here, surges are not as large as in Trace 1, but occur much more frequently.
*X* Again, we study the unavailable period when the ESD size is reduced, and find that
*X* if we reduce the ESD size by 50%, the unavailability is 6.2% of the total time. Based on our observations, since the unavailability is manageable, we can use power capping during these periods without hurting performance significantly.
*X* We conclude that sizing the ESD to only cover typical-case power surges does not greatly impact performance.

## Slide 13: SizeCap: Key Ideas
Key Idea 1: Size ESD based on typical-case power surges, not worst-case surges
Key Idea 2: Use smart power capping to handle remaining power surges
Notes: However, since power capping still hurts performance during unavailable periods,
*X* we want to develop a smarter approach to power capping to minimize the performance degradation.

## Slide 14: Key Idea 2: Smart Power Capping
Make power capping aware of fuel cell load following behavior
  Fuel cells respond differently to different power surges
  With fuel cell load following model, we can know how fuel cell power responds to rack power demand
  Control the rack power such that it never exceeds sum of fuel cell power and ESD output
Make power capping aware of workload behavior
  Workload performance is dependent on how power is allocated over time
  Allocate power over time to maximize workload performance
Smart power capping uses fuel cell,
workload behavior to deliver higher benefits
Notes: One way to make power capping smarter is to expose it to the load following behavior of fuel cells.
*X* As we saw already, the fuel cell response rate is dependent on the characteristics of the power surge.
*X* Power capping can improve performance while still preventing shortfalls if it determines the fuel cell response, and ensures that the rack power demand never exceeds the sum of this response and the output of the ESD.
*X* We can also make power capping smarter by exposing it to the behavior of the workload currently running on the system.
*X* The long-term performance of a workload is dependent on how we allocate power to it over time.
*X* As a result, if we know how the workload is expected to behave in the near future, we can make long-term power allocation decisions that maximize the workload performance over time.
*X* In summary, we use smart power capping policies that are aware of fuel cell and workload behavior to deliver greater performance.

## Slide 15: SizeCap
A framework to reduce ESD capacity by employing smart power capping policies
At design time
  Select best power capping policy implementable in system
  Find minimum ESD size that still meets service level agreement (SLA) under the selected policy
At runtime
  Period-based power control
  Every period: use power capping policy to determine power used by each server in next period
Notes: Based on these two key ideas, we propose SizeCap. SizeCap is a framework that works to reduce the ESD capacity significantly while still avoiding power shortfalls, by catering the ESD size only to typical-case power surges, and by employing smart power capping policies. SizeCap consists of two parts.
*X* At design time, it selects the best of the power capping policies that can be implemented within the system. Using this policy, it finds the minimum size of the ESD that still meets the data center SLA.
*X* Once the system is constructed, SizeCap includes power control logic that runs in a rack at every period. Whenever the controller runs, it uses the selected power capping policy to determine the power used by each server for the upcoming period.

## Slide 16: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: So let’s look at the detailed design of SizeCap.

## Slide 17: Design Time: Policy Selection & ESD Sizing
ESD Capacity
+
Power Capping
Policy
ESD Sizing Engine
Power Capping Policy Pool
Representative
Workload/Trace
Service Level
Agreement (SLA)
Power Capping
Constraints
SizeCap
Best
Capping
Policy
Notes: The design time part of the framework starts with
*X* a pool of potential power capping policies.
*X* From this pool, we use the design constraints of the current system to eliminate policies that are not implementable with the existing resources.
*X* Then, SizeCap selects the best of the remaining policies.
*X* SizeCap then runs its ESD sizing engine,
*X* which uses a representative trace,
*X* along with the SLA,
*X* to determine the smallest ESD capacity possible
*X* under the selected policy. The ESD is sized to ensure that the system will never experience a power shortfall.
*X* We then output the capacity and policy, for the data center designer to implement.

## Slide 18: Runtime: Execute Power Capping Policy
Power Budget Planner: Plan total rack power budget for next period
Power Budget Assigner: Distribute rack power among the servers for next period
Controller can be centralized or decentralized
Fuel Cell
System Info
Power
Budget
Assigner
ESD
Fuel Cell System
Power
Budget
Planner
Server Power Budget(s)
Server Info(s)
Server(s)
Rack Power
Budget
Power Capping Controller
ESD
Energy
Notes: Once the system is built, we execute the power capping policy periodically at runtime..
*X* We add a power capping controller
*X* This includes a power budget planner
*X* that determines the total power budget available for the rack, using information
*X* from the fuel cell system and
*X* from the ESD.
*X* In some cases, the planner also uses information from the servers.
*X* Once we have the rack power budget, we send this information to the
*X* power budget assigner,
*X* whose job is to
*X* distribute this power among the individual servers.
*X* This controller can either be implemented centrally, with a single controller for the entire rack, or in a decentralized manner, where each server has its own controller.

## Slide 19: Power Capping Policy Taxonomy
Power Capping Policy
C
FCA
WA
D
FCA
WA
C
FCA
WU
D
FCA
WU
C
FCU
WA
D
FCU
WA
C
FCU
WU
D
FCU
WU
FCA
WA
FCA
WU
FCU
WA
FCU
WU
FCA
FCU
Fuel Cell Model
Aware vs. Unaware
Workload
Aware vs. Unaware
Centralized vs.
Decentralized
Notes: As we discussed before, we develop smart power capping policies that have different degrees of awareness. Here, we present a taxonomy of the different combinations possible.
*X* First, the policy can be aware or unaware of the fuel cell behavior.
*X* Second, the policy can be aware or unaware of the expected workload behavior.
*X* Finally, the policies can be centralized or decentralized.
While this gives us eight combinations in all,
*X* we remove three of them, due to communication limitations or potential power failures. We discuss why these policies are not feasible in detail in our paper.

## Slide 20: Power Capping Policy Taxonomy
Power Capping Policy
C
FCA
WA
C
FCA
WU
D
FCA
WU
C
FCU
WU
D
FCU
WU
FCA
WA
FCA
WU
FCU
WU
FCA
FCU
Fuel Cell Model
Aware vs. Unaware
Workload
Aware vs. Unaware
Centralized vs.
Decentralized
Fuel Cell Unaware
Workload Unaware
Notes: *X* First, let’s look at the fuel cell and workload unaware policies.

## Slide 21: Fuel Cell and Workload Unaware Policies
  Goal: No power shortfalls, optimize performance in next period
  Power Budget Planner
    Use ESD first
    When ESD is used up
      Ramp up rack power with conservative but safe rate
      Static rate that guarantees no shortfalls in entire fuel cell operating range
  Power Budget Assigner
    Assign power to each server proportional to each server’s workload intensity or current power consumption
Notes: Here, our goal is to ensure that no power shortfalls occur, and to optimize the performance in the next capping period.
*X* In the controller, the power budget planner first
*X* uses the energy buffered in the ESD.
*X* When this energy is used up, we must rely on power capping. Recall that the fuel cell is load following. For the fuel cell to increase its power output, the capping needs to increase the load exerted on the fuel cell.
*X* Since the capping policy is unaware of detailed fuel cell behavior, we choose to ramp up the rack at a safe rate.
*X* This is a static rate that guarantees that wherever we are in the operating range of the fuel cell, the increased power demand will never incur a power shortfall.
*X* The power budget assigner will assign server power for the next period, by partitioning the total rack power up among the servers proportional to the server’s workload intensity or current power consumption

## Slide 22: Power Capping Policy Taxonomy
Power Capping Policy
C
FCA
WA
C
FCA
WU
D
FCA
WU
C
FCU
WU
D
FCU
WU
FCA
WA
FCA
WU
FCU
WU
FCA
FCU
Fuel Cell Model
Aware vs. Unaware
Workload
Aware vs. Unaware
Centralized vs.
Decentralized
Fuel Cell Aware
Workload Unaware
Notes: What happens if we expose
*X* the operating behavior of the fuel cell to our power capping controller?

## Slide 23: Fuel Cell Aware, Workload Unaware Policies
  Goal: No power shortfalls, optimize performance in next period
  Power Budget Planner
    Use ESD first
    When ESD is used up
      Ramp up rack power with maximum safe ramp rate
      Dynamically adapted rate to guarantee no shortfalls only under current conditions, derived from fuel cell model
  Power Budget Assigner
    Same as fuel cell and workload unaware policies
Notes: For such policies, our goal remains the same.
*X* Again, the power budget planner first uses the energy in the ESD.
*X* Now, when this energy is used up,
*X* the controller ramps up the rack power at the maximum safe rate.
*X* This rate is derived from a model of the fuel cell operating behavior, and is dynamically adapted to the fuel cells’ current conditions, maximizing their power output increase while still guaranteeing that no shortfalls occur.
*X* The power budget assigner remains the same as for our unaware policies.

## Slide 24: Power Capping Policy Taxonomy
Power Capping Policy
C
FCA
WA
C
FCA
WU
D
FCA
WU
C
FCU
WU
D
FCU
WU
FCA
WA
FCA
WU
FCU
WU
FCA
FCU
Fuel Cell Model
Aware vs. Unaware
Workload
Aware vs. Unaware
Centralized vs.
Decentralized
Fuel Cell Aware
Workload Aware
Notes: Finally, we come to the
*X* policies that are both fuel cell and workload aware.

## Slide 25: Fuel Cell and Workload Aware Policy
  Goal: No power shortfalls, optimize performance over multiple periods
    Spend max ESD power now, cap aggressively in later periods
    Save some power now and cap more, use power in later periods
  Power Budget Planner
    Use fuel cell model to find all safe power capping settings
    Use workload behavior to assign power
      Look at how workload performs over next several periods under different power allocations
      Pick power capping setting that maximizes long-term performance
  Power Budget Assigner
    Similar to previous policies
Notes: In this case, we change our goal. Before, we were optimizing performance only for the next period. Now, we will aim to optimize longer-term performance, spanning multiple capping periods.
*X* For example, for some workloads, you will get the best performance if you spend the maximum ESD power now to avoid power capping, but use capping aggressively in later periods when the workload intensity is low.
*X* For other workloads, it may be better to save some of the ESD power now and employ capping earlier, which will allow us to use the saved ESD power, along with less aggressive capping, in later periods.
*X* For this controller, the power budget planner becomes more sophisticated,
*X* using the fuel cell model to find all of the safe power capping settings.
*X* Then, it uses the workload behavior to assign the power.
*X* To do this, it looks at the expected performance of the workload over the next several periods, using a series of different safe power allocations.
*X* From these different allocations, we pick the settings that maximize performance in the long term.
*X* While the planner changes significantly, the power budget assigner remains similar to the ones used in our previous policies.

## Slide 26: Outline
Background
Problem
Existing Approaches
Key Ideas
Detailed Design
Evaluation
Conclusion
Notes: Now, let’s take a look at how SizeCap performs.

## Slide 27: Evaluation Methodology
Simulation Configuration
  Rack with 45 production servers
  Each server runs power capping driver developed in-house
Traces
  Production traces collected from Microsoft data centers
  WebSearch workload
Metrics
  Success rate: Percentage of requests completed within the maximum allowable service time
  Average latency: Average service latency of all requests
  P95 latency: 95th percentile (tail) latency
Notes:   For our evaluations,
  *X* we simulate a rack with 45 production servers.
  *X* We use workload intensity traces collected from production data centers at Microsoft, which are input to the WebSearch workload.
  *X* In our evaluations, we study three metrics. First, the success rate is the percentage of requests completed within the maximum allowable service time defined by the SLA. We also show performance using average latency, as well as using P95, or tail, latency.

## Slide 28: Key Evaluation Results
SLA: Assume margins of 0.1% success rate, 3% average latency, and 10% P95 latency under fully-provisioned ESD
D-FCA-WU: Safely reduces ESD size by 85% for Trace 1, by 50% for Trace 2, and meets SLA
Policies with awareness of fuel cell and/or workload behavior reduce ESD size 10–20% more than unaware policies
Notes: In the interests of time, we present only our key evaluation results. Here, we again show the two traces that we focus on in our study.
To see how much we can reduce our ESD by, we assume that there are some margins, or slack, available in the SLA when we use a fully-sized ESD.
*X* In these evaluations, we assume a 0.1% margin for success rate, a 3% margin for average latency, and a 10% tail latency margin.
*X* We find that even for our fuel cell aware, workload unaware capping policy, which is not the smartest of our policies but is easily implementable, we can safely reduce the ESD size significantly. For the large, infrequent surge behavior seen in Trace 1, we can reduce the ESD size by 85%, and for the smaller but more frequent surges observed in Trace 2, we can reduce the ESD size by 50%. In both cases, we still meet the SLA.
*X* We also find that capping policies with some form of awareness can reduce the ESD size 10 to 20 percent more than the unaware policies. We encourage you to check out our paper for more detailed results.
113kJ
68kJ

## Slide 29: Conclusion
Fuel cells: efficient power source for data centers
Problem: limited load following capability
  Fuel cells only gradually increase output power when load increases
  Power surges may lead to a power shortfall  server shutdown or damage
Existing Approaches
  Power capping: hurts performance
  Energy storage device (ESD): increases cost
Our Approach: SizeCap
  Our goal: low cost, still guarantee workload performance
  Key Idea 1: Size the ESD to cover only typical-case power surges
  Key Idea 2: Use smart power capping, which is aware of fuel cell and workload behavior, to handle remaining power surges
  SizeCap safely reduces ESD size by 50 – 85%
Notes: To conclude, fuel cells are an efficient power source for data centers.
*X* However, their limited load following capability is a problem.
*X* Fuel cells only gradually increase their output when the power demand increases,
*X* and surges can lead to a power shortfall.
*X* We find that existing approaches are undesirable, *X* as power capping greatly hurts performance,
*X* while fully-provisioned ESDs greatly increase cost.
*X* We propose SizeCap, an efficient solution
*X* to avoid power shortfalls at low cost while still guaranteeing workload performance under an SLA.
*X* In SizeCap, we reduce the ESD size so that they cover only typical-case power surges,
*X* and then use smart power capping to handle the rare remaining power surges.
*X* By doing so, SizeCap can safely reduce the size of the ESD by as much as 85%.

## Slide 30: SizeCap: Efficiently Handling Power Surges for Fuel Cell Powered Data Centers
Yang Li, Di Wang, Saugata Ghose, Jie Liu,
Sriram Govindan, Sean James, Eric Peterson,
John Siegler, Rachata Ausavarungnirun, Onur Mutlu
Notes: Thank you for your time, and I’m happy to take any questions.

## Slide 31: Impact of ESD Cost on TCO
ESD cost
  Supercapacitor: $5.6 per kJ [McCawley, Fung Institute 2014]
ESD sizes for our traces
  Trace 1
    Fully-provisioned: 112.5 kJ per rack  $630.00
    After SizeCap: 16.9 kJ per rack  $94.50
  Trace 2
    Fully-provisioned: 68.0 kJ per rack  $380.80
    After SizeCap: 34.0 kJ per rack  $190.40